## Space Loads
Classroom Loads (No Ventilation Air)
| Classroom 1 |  | Classroom 2 |  | Classroom 3 |  | Classroom 4 |  | Classroom 5 |  | Classroom 6 |  | East Wing Corridor
Hour of Design Day | Sensible Heating Load (BTU/Hr) | Total Cooling Load (BTU/Hr) | Sensible Heating Load (BTU/Hr) | Total Cooling Load (BTU/Hr) | Sensible Heating Load (BTU/Hr) | Total Cooling Load (BTU/Hr) | Sensible Heating Load (BTU/Hr) | Total Cooling Load (BTU/Hr) | Sensible Heating Load (BTU/Hr) | Total Cooling Load (BTU/Hr) | Sensible Heating Load (BTU/Hr) | Total Cooling Load (BTU/Hr) | Sensible Heating Load (BTU/Hr) | Total Cooling Load (BTU/Hr)
1 | -24308.1 | 9640.9 | -24284 | 9593.7 | -23369.5 | 9372.8 | -23345.3 | 9325.7 | -28281.6 | 10818.7 | -28246.4 | 10725.9 | -27005.6 | 9308
2 | -24725.6 | 9252.2 | -24701.5 | 9194.6 | -23787 | 8984.5 | -23762.8 | 8927 | -28738.7 | 10371.2 | -28703.5 | 10272.8 | -27486.1 | 8866.7
3 | -25088.3 | 8903.4 | -25064.2 | 8838.2 | -24150 | 8638.8 | -24125.9 | 8573.8 | -29135.9 | 9971.9 | -29100.7 | 9870.1 | -27908.7 | 8473.9
4 | -25318.2 | 8676.5 | -25294.1 | 8606.5 | -24380.6 | 8417.5 | -24356.4 | 8347.5 | -29384.8 | 9713.1 | -29349.6 | 9610.1 | -28280.8 | 8123.7
5 | -25558.8 | 8430.1 | -25534.7 | 8357.3 | -24622 | 8178.4 | -24597.9 | 8105.6 | -29646.8 | 9436.7 | -29611.6 | 9334.1 | -28608.7 | 7809.8
6 | -25775.4 | 8428.5 | -25751.4 | 10543.5 | -24839.7 | 8185.7 | -24815.7 | 10300.8 | -29882.9 | 9524.6 | -29847.7 | 12738.8 | -28897.6 | 7795.2
7 | -25967.4 | 8590.1 | -25943.4 | 13045.7 | -25032.9 | 8357.4 | -25008.8 | 12813 | -30092.1 | 9843.8 | -30056.9 | 16609.9 | -29152.4 | 8035.5
8 | -30609 | 10856.1 | -30584 | 15932.7 | -29676.3 | 10634.5 | -29651.3 | 15711.1 | -35240.8 | 12536.2 | -35204.2 | 20258.8 | -36137.6 | 11120.1
9 | -30728.3 | 21177.7 | -30702.6 | 25672.5 | -29797.7 | 20967.6 | -29772 | 25462.5 | -35780.8 | 23043.2 | -35743.1 | 29946.7 | -41476.6 | 11919.8
10 | -29297.9 | 22212.5 | -29272.1 | 25421.2 | -28369.1 | 22014.1 | -28343.3 | 25222.8 | -34243.3 | 24244.5 | -34205.5 | 29257.2 | -40212.7 | 12952.1
11 | -28265.7 | 23086.4 | -28239.9 | 24543.7 | -27338.5 | 22899.1 | -27312.6 | 24356.5 | -33128.7 | 25270.8 | -33090.8 | 27636.9 | -39217.5 | 14155.4
12 | -27432.2 | 23856.8 | -27406.3 | 24105.5 | -26506.1 | 23679.4 | -26480.3 | 23928.3 | -32226.6 | 26169.8 | -32188.7 | 26571.5 | -38371.8 | 15329.7
13 | -26731.6 | 24676.5 | -26705.8 | 24743.7 | -25806.4 | 24506.7 | -25780.6 | 24574 | -31467.6 | 27244.2 | -31429.6 | 27259.4 | -37638.3 | 16224
14 | -26132.3 | 26774.7 | -26106.5 | 25284.5 | -25207.4 | 26609.1 | -25181.6 | 25119 | -30817.8 | 30273.4 | -30779.8 | 27838 | -36996.7 | 16734.4
15 | -25614.8 | 28913.5 | -25588.9 | 25698.2 | -24689.8 | 28747.8 | -24663.9 | 25532.7 | -30256.3 | 33289.3 | -30218.3 | 28249.1 | -36433.3 | 16901.9
16 | -25165.5 | 30426.3 | -25139.6 | 25962.3 | -24239.9 | 30255.7 | -24214 | 25791.9 | -29768.8 | 35349.4 | -29730.7 | 28463.4 | -35937.7 | 16893.7
17 | -24773.9 | 30984.8 | -24748 | 26061.6 | -23847.4 | 30804.9 | -23821.5 | 25882 | -29343.8 | 36011.6 | -29305.8 | 28465.9 | -35501.3 | 16797.9
18 | -23533.6 | 20275.5 | -23508.4 | 16193 | -22605.4 | 20082.6 | -22580.1 | 16000.4 | -27566.7 | 24699 | -27529.7 | 18432.2 | -28802.4 | 16478.5
19 | -17757.2 | 16364.7 | -17732.9 | 15202 | -16826.8 | 16156.7 | -16802.6 | 14994.3 | -21049.2 | 19029.4 | -21013.6 | 17185.4 | -19559.8 | 15833.6
20 | -20745.2 | 12654 | -20721.1 | 12610.7 | -19812.8 | 12430.4 | -19788.6 | 12387.4 | -24386.9 | 14330.9 | -24351.4 | 14184.9 | -23238.8 | 12527.9
21 | -21737.2 | 11873.9 | -21713 | 11859.6 | -20802.9 | 11635.8 | -20778.7 | 11621.8 | -25468.3 | 13414.1 | -25432.9 | 13320.1 | -24275.4 | 11711.6
22 | -22590.8 | 11149.5 | -22566.7 | 11137.6 | -21654.9 | 10899.2 | -21630.8 | 10887.5 | -26402.7 | 12568.2 | -26367.4 | 12489.6 | -25115.3 | 11000.1
23 | -23261 | 10571.9 | -23237 | 10550.6 | -22323.8 | 10312.3 | -22299.7 | 10291.2 | -27135.8 | 11894.9 | -27100.5 | 11815.9 | -25833.9 | 10368.2
24 | -23824.7 | 10076.4 | -23800.7 | 10041.9 | -22886.6 | 9810.9 | -22862.5 | 9776.6 | -27752.6 | 11320.9 | -27717.3 | 11235.4 | -26458.7 | 9806.5
PEAK | 30728.3 | 30984.8 | 30702.6 | 26061.6 | 29797.7 | 30804.9 | 29772 | 25882 | 35780.8 | 36011.6 | 35743.1 | 29946.7 | 41476.6 | 16901.9
|  |  |  | Peak cooling sensible heat ratio (SHR) for all classrooms = | 0.7

## Outdoor Air Loads
|  | winter design condition: |  | 0 | oF DB
Ventilation Air Requirements and Loads |  | summer design condition: |  | 90 | oF DB
|  |  |  | 74 | oF WB
Room Common Name | Est. Max. | cfm/ | Total | Heating | Cooling
| Occupancy | person | Ventilation | Ventilation Air | Ventilation Air | Ventilation Air
|  |  |  | Air Load | Air Load | Air Load
| OR | OR | Air | Sensible Load | Sensible Load | Latent Load
| area (ft2) for | cfm/ft2 for
| corridors | corridors
EAST WING |  |  | (cfm) | (Btu/hr) | (Btu/hr) | (Btu/hr)
Classroom 1 | 30 | 15 | 450 | 34992 | 8748 | 10018.8
Classroom 2 | 30 | 15 | 450 | 34992 | 8748 | 10018.8
Classroom 3 | 30 | 15 | 450 | 34992 | 8748 | 10018.8
Classroom 4 | 30 | 15 | 450 | 34992 | 8748 | 10018.8
Classroom 5 | 30 | 15 | 450 | 34992 | 8748 | 10018.8
Classroom 6 | 30 | 15 | 450 | 34992 | 8748 | 10018.8
Corridor in East Wing | 1650 | 0.1 | 165 | 12830.4 | 3207.6 | 3673.56
TOTALS |  |  | 2865 | 222782.4 | 55695.6 | 63786.36
Loads in tons |  |  |  | 18.5652 | 4.6413 | 5.3155